## Model inputs
ORC
Parameter |  | Value | Unit
Heat source | Heat source inlet temperature | 473 | K
| Heat source outlet temperature | 423 | K
| Heat source mass-flow rate | 1 | kg/s
| Heat source specific heat capacity | 1000 | J/kg K
Heat sink | Heat sink inlet temperature | 288 | K
| Heat sink mass-flow rate | 1 | kg/s
| Heat sink specific heat capacity | 4200 | J/kg K
Component | Pump isentropic efficiency | 70 | %
| Expander isentropic efficiency | 80 | %
| Recuperator effectiveness | 70 | %
Fixed ORC | Condensation temperature | 313 | K
| Pump subcooling | 2 | K
| Expander inlet parameter | 1.2 | -
Heat pump (R1233zd(E), n-pentane)
Parameter |  | Value | Unit
Heat source | Heat source inlet temperature | 323 | K
| Heat source outlet temperature | 318 | K
| Heat source mass-flow rate | 1 | kg/s
| Heat source specific heat capacity | 4200 | J/kg K
Heat sink | Heat sink inlet temperature | 328 | K
| Heat sink mass-flow rate | 1 | kg/s
| Heat sink specific heat capacity | 4200 | J/kg K
Component | Compressor isentropic efficiency | 70 | %
Fixed ORC | Evaporation temperature | 313 | K
| Compressor superheat | 5 | K
| Expansion valve subcooling | 5 | K
| Internal heat exchanger temperature difference | 15 | K

## ORC_R1233zd(E)
Evaporation pressure [bar] | Pressure-ratio | Efficiency (cycle) [%] | Efficiency (exergy) [%] | Mass flow [kg/s] | Net [kW] | Pump [kW] | Turbine [kW] | Heater [kW] | Cooler [kW] | Recup.[kW] | UA (hot) [kW/K] | UA (cold) [kW/K] | UA (rec.) [kW/K] | Pinch (hot) [K] | Pinch (cold) [K] | Pinch (rec.) [K]
4.2736 | 2 | 5.517 | 6.551 | 0.241 | 2.759 | 0.058 | 2.817 | 50 | 47.241 | 4.975 | 0.46 | 2.472 | 0.319 | 89.129 | 14.26 | 12.324
7.3591 | 3.444 | 9.361 | 11.114 | 0.23 | 4.68 | 0.136 | 4.816 | 50 | 45.32 | 5.12 | 0.554 | 2.334 | 0.312 | 73.798 | 14.732 | 12.893
10.4468 | 4.889 | 11.583 | 13.753 | 0.224 | 5.792 | 0.211 | 6.002 | 50 | 44.208 | 5.217 | 0.638 | 2.256 | 0.31 | 62.817 | 15.007 | 13.194
13.5324 | 6.333 | 13.075 | 15.523 | 0.22 | 6.537 | 0.283 | 6.821 | 50 | 43.463 | 5.261 | 0.718 | 2.204 | 0.309 | 54.198 | 15.189 | 13.291
16.62 | 7.778 | 14.148 | 16.798 | 0.217 | 7.074 | 0.355 | 7.429 | 50 | 42.926 | 5.257 | 0.797 | 2.168 | 0.31 | 47.129 | 15.316 | 13.217
19.7056 | 9.222 | 14.947 | 17.746 | 0.215 | 7.473 | 0.427 | 7.9 | 50 | 42.527 | 5.206 | 0.876 | 2.142 | 0.311 | 41.198 | 15.406 | 12.993
22.7932 | 10.667 | 15.548 | 18.46 | 0.214 | 7.774 | 0.498 | 8.273 | 50 | 42.226 | 5.109 | 0.953 | 2.123 | 0.314 | 36.181 | 15.468 | 12.624
25.8788 | 12.111 | 15.996 | 18.992 | 0.213 | 7.998 | 0.57 | 8.568 | 50 | 42.002 | 4.963 | 1.026 | 2.11 | 0.316 | 31.958 | 15.506 | 12.109
28.9665 | 13.556 | 16.315 | 19.37 | 0.213 | 8.157 | 0.643 | 8.801 | 50 | 41.843 | 4.761 | 1.091 | 2.102 | 0.32 | 28.5 | 15.523 | 11.436
32.052 | 15 | 16.512 | 19.604 | 0.213 | 8.256 | 0.717 | 8.973 | 50 | 41.744 | 4.478 | 1.136 | 2.098 | 0.322 | 25.903 | 15.524 | 10.686

## ORC_n-pentane
Evaporation pressure [bar] | Pressure-ratio | Efficiency (cycle) [%] | Efficiency (exergy) [%] | Mass flow [kg/s] | Net [kW] | Pump [kW] | Turbine [kW] | Heater [kW] | Cooler [kW] | Recup.[kW] | UA (hot) [kW/K] | UA (cold) [kW/K] | UA (rec.) [kW/K] | Pinch (hot) [K] | Pinch (cold) [K] | Pinch (rec.) [K]
2.2964 | 2 | 5.337 | 6.337 | 0.124 | 2.669 | 0.033 | 2.701 | 50 | 47.331 | 5.936 | 0.458 | 2.469 | 0.368 | 88.777 | 14.336 | 13.421
4.5928 | 4 | 10.145 | 12.045 | 0.117 | 5.072 | 0.092 | 5.164 | 50 | 44.928 | 6.714 | 0.585 | 2.288 | 0.358 | 68.955 | 14.988 | 15.582
6.8892 | 6 | 12.694 | 15.071 | 0.113 | 6.347 | 0.147 | 6.494 | 50 | 43.653 | 7.26 | 0.702 | 2.192 | 0.354 | 55.612 | 15.347 | 17.078
9.1856 | 8 | 14.369 | 17.06 | 0.11 | 7.184 | 0.201 | 7.385 | 50 | 42.816 | 7.67 | 0.823 | 2.13 | 0.351 | 45.333 | 15.588 | 18.192
11.482 | 10 | 15.579 | 18.497 | 0.108 | 7.79 | 0.254 | 8.043 | 50 | 42.21 | 7.987 | 0.955 | 2.085 | 0.349 | 36.914 | 15.765 | 19.043
13.7784 | 12 | 16.501 | 19.592 | 0.106 | 8.251 | 0.305 | 8.556 | 50 | 41.749 | 8.233 | 1.103 | 2.051 | 0.348 | 29.777 | 15.9 | 19.69
16.0748 | 14 | 17.226 | 20.453 | 0.105 | 8.613 | 0.356 | 8.97 | 50 | 41.387 | 8.42 | 1.277 | 2.024 | 0.347 | 23.602 | 16.005 | 20.168
18.3712 | 16 | 17.806 | 21.141 | 0.104 | 8.903 | 0.407 | 9.31 | 50 | 41.097 | 8.554 | 1.486 | 2.003 | 0.347 | 18.194 | 16.088 | 20.494
20.6676 | 18 | 18.272 | 21.695 | 0.103 | 9.136 | 0.458 | 9.594 | 50 | 40.864 | 8.639 | 1.75 | 1.987 | 0.348 | 13.433 | 16.152 | 20.673
22.964 | 20 | 18.645 | 22.137 | 0.103 | 9.322 | 0.509 | 9.832 | 50 | 40.678 | 8.671 | 2.104 | 1.974 | 0.348 | 9.248 | 16.2 | 20.702

## ORC_MM
Evaporation pressure [bar] | Pressure-ratio | Efficiency (cycle) [%] | Efficiency (exergy) [%] | Mass flow [kg/s] | Net [kW] | Pump [kW] | Turbine [kW] | Heater [kW] | Cooler [kW] | Recup.[kW] | UA (hot) [kW/K] | UA (cold) [kW/K] | UA (rec.) [kW/K] | Pinch (hot) [K] | Pinch (cold) [K] | Pinch (rec.) [K]
0.2324 | 2 | 3.969 | 4.712 | 0.2 | 1.985 | 0.004 | 1.989 | 50 | 48.015 | 8.603 | 0.471 | 2.494 | 0.536 | -91.687 | 14.446 | 14.027
0.723 | 6.222 | 9.942 | 11.804 | 0.182 | 4.971 | 0.02 | 4.991 | 50 | 45.029 | 11.008 | 0.595 | 2.247 | 0.512 | 67.679 | 15.402 | 18.82
1.2136 | 10.444 | 12.447 | 14.778 | 0.174 | 6.224 | 0.035 | 6.258 | 50 | 43.776 | 12.286 | 0.722 | 2.141 | 0.5 | 54.292 | 15.831 | 21.576
1.7043 | 14.667 | 14.009 | 16.632 | 0.168 | 7.004 | 0.049 | 7.053 | 50 | 42.996 | 13.184 | 0.847 | 2.074 | 0.492 | 44.544 | 16.108 | 23.601
2.1949 | 18.889 | 15.128 | 17.961 | 0.164 | 7.564 | 0.062 | 7.626 | 50 | 42.436 | 13.884 | 0.98 | 2.025 | 0.485 | 36.735 | 16.313 | 25.225
2.6855 | 23.111 | 15.99 | 18.984 | 0.161 | 7.995 | 0.076 | 8.07 | 50 | 42.005 | 14.458 | 1.128 | 1.987 | 0.48 | 30.155 | 16.474 | 26.591
3.1761 | 27.333 | 16.685 | 19.81 | 0.159 | 8.343 | 0.089 | 8.431 | 50 | 41.657 | 14.947 | 1.298 | 1.956 | 0.476 | 24.435 | 16.607 | 27.774
3.6668 | 31.556 | 17.264 | 20.497 | 0.157 | 8.632 | 0.101 | 8.733 | 50 | 41.368 | 15.371 | 1.503 | 1.93 | 0.472 | 19.357 | 16.719 | 28.818
4.1574 | 35.778 | 17.756 | 21.082 | 0.155 | 8.878 | 0.114 | 8.992 | 50 | 41.122 | 15.746 | 1.761 | 1.908 | 0.469 | 14.777 | 16.816 | 29.753
4.648 | 40 | 18.183 | 21.588 | 0.153 | 9.091 | 0.127 | 9.218 | 50 | 40.909 | 16.082 | 2.108 | 1.888 | 0.466 | 10.6 | 16.901 | 30.598

## HP_R1233zd(E)
Pressure ratio | Coefficient of performance [-] | Compressor work [kW] | Heater [kW] | Cooler [kW] | Recup. [kW] | Mass flow [kg/s] | UA (hot) [kW/K] | UA (cold) [kW/K] | UA (rec.) [kW/K] | Pinch (hot) [K] | Pinch (cold) [K] | Pinch (rec.) [K]
2 | 9.902 | 2.359 | 23.359 | 21 | 1.504 | 0.118 | 3.955 | 2.93 | nan | 3.523 | 5 | 1.477
2.889 | 6.212 | 4.029 | 25.029 | 21 | 1.676 | 0.131 | 1.226 | 2.933 | 0.111 | 17.359 | 5 | 12.64
3.778 | 4.776 | 5.562 | 26.562 | 21 | 1.849 | 0.144 | 0.842 | 2.935 | 0.07 | 28.203 | 5 | 23.757
4.667 | 3.975 | 7.058 | 28.058 | 21 | 2.03 | 0.159 | 0.688 | 2.937 | 0.057 | 37.222 | 5 | 33.042
5.556 | 3.448 | 8.579 | 29.579 | 21 | 2.224 | 0.174 | 0.607 | 2.94 | 0.05 | 44.989 | 5 | 41.076
6.444 | 3.064 | 10.173 | 31.173 | 21 | 2.437 | 0.19 | 0.56 | 2.943 | 0.047 | 51.834 | 5 | 48.194
7.333 | 2.767 | 11.888 | 32.888 | 21 | 2.674 | 0.209 | 0.53 | 2.946 | 0.046 | 57.962 | 5 | 54.609
8.222 | 2.524 | 13.775 | 34.775 | 21 | 2.943 | 0.23 | 0.514 | 2.949 | 0.046 | 63.513 | 5 | 60.463
9.111 | 2.321 | 15.901 | 36.901 | 21 | 3.255 | 0.254 | 0.506 | 2.953 | 0.047 | 68.58 | 5 | 65.859
10 | 2.144 | 18.353 | 39.353 | 21 | 3.622 | 0.283 | 0.506 | 2.958 | 0.049 | 73.232 | 5 | 70.873

## HP_n-pentane
Pressure ratio | Coefficient of performance [-] | Compressor work [kW] | Heater [kW] | Cooler [kW] | Recup. [kW] | Mass flow [kg/s] | UA (hot) [kW/K] | UA (cold) [kW/K] | UA (rec.) [kW/K] | Pinch (hot) [K] | Pinch (cold) [K] | Pinch (rec.) [K]
2 | 10.428 | 2.228 | 23.228 | 21 | 1.633 | 0.06 | 4.764 | 2.932 | nan | 2.651 | 5 | 1.468
2.889 | 6.546 | 3.787 | 24.787 | 21 | 1.809 | 0.067 | 1.327 | 2.934 | 0.137 | 15.856 | 5 | 11.225
3.778 | 5.037 | 5.202 | 26.202 | 21 | 1.984 | 0.073 | 0.899 | 2.936 | 0.082 | 26.18 | 5 | 21.889
4.667 | 4.199 | 6.565 | 27.565 | 21 | 2.163 | 0.08 | 0.729 | 2.939 | 0.065 | 34.74 | 5 | 30.789
5.556 | 3.649 | 7.928 | 28.928 | 21 | 2.352 | 0.087 | 0.639 | 2.941 | 0.057 | 42.09 | 5 | 38.488
6.444 | 3.251 | 9.327 | 30.327 | 21 | 2.553 | 0.094 | 0.585 | 2.944 | 0.053 | 48.545 | 5 | 45.308
7.333 | 2.945 | 10.795 | 31.795 | 21 | 2.772 | 0.102 | 0.551 | 2.947 | 0.051 | 54.303 | 5 | 51.454
8.222 | 2.699 | 12.362 | 33.362 | 21 | 3.012 | 0.111 | 0.529 | 2.95 | 0.05 | 59.496 | 5 | 57.065
9.111 | 2.493 | 14.062 | 35.062 | 21 | 3.279 | 0.121 | 0.516 | 2.953 | 0.05 | 64.213 | 5 | 62.239
10 | 2.318 | 15.935 | 36.935 | 21 | 3.579 | 0.132 | 0.51 | 2.957 | 0.051 | 68.517 | 5 | 67.048